## RP Category Calculator
Remote Power Category Calculator
Applications in a bundle: | IEEE Standard | Power | Current | Energized pairs | Percentage in bundle | unused | Ic average | Remote Power Category
No PoE | - | 0 | 0 | 0 | 0% |  | 0.5 | RP3
PoE Type 1 (PoE) | 802.3af | 15 | 0.175 | 2 | 0% | 0%
PoE Type 2 (PoEP) | 802.3at | 30 | 0.3 | 2 | 0% | 0%
PoE Type 3 (4PPoE) | 802.3bt | 60 | 0.3 | 4 | 0% | 0%
PoE Type 4 (4PPoE) | 802.3bt | 90 | 0.5 | 4 | 100% | 100%
Yellow fields can be modified

## Link Length Calculator
Permanent Link length calculator according to ISO/IEC 14763-2 and EN 50174-2:
PoE-Application Category: |  | RP3 | [6 empty] | Power: | 90 | W
Class: |  | D
Connectors in Channel |  | 2 |  | Shielding: | /s |  |  |  | Note: | No restrictions on the use of 4PPoE. Temperature increase expected.
Total patchcord length: |  | 10 | m
Patchcord coefficient: |  | 1.5
Max. cable temprature: |  | 60 | °C | STP Prio: | No |  |  |  | Standard channel length: | 109 | m
Link segment no. | Cable type | Attenuation reserve of cable for app. Class | Installation cable diameter (mm) | Cable resistance (Ω/100m) | Ambient temp. (°C) | Number of cables | Contain-ment width (mm) | Width to Height Ratio | Bundle reduction factor | Installation condition | Temp. increase bundle (°C) | Total temp. (ambient + increase) (°C) | Attenuation factor (% pro ºC) | Planned segment length (m) | Normalized electrical length at 20 °C (m)
PC1 | Patch Cord at Patch Panel side | 0.66667 | 6 | 13 | 35 | 24 | 0 | 0 | 1 | E/F: Ventilated | 8.6312 | 43.6312 | 0.2 | 5 | 7.8545
1 | Cat5e/s (AWG24) | 1 | 5 | 9.5 | 25 | 200 | 200 | 8.9604 | 0.52858 | E/F: Ventilated | 16.2437 | 41.2437 | 0.2 | 40 | 41.6995
2 | Cat5e/s (AWG24) | 1 | 5 | 9.5 | 25 | 75 | 100 | 5.9144 | 0.62129 | C: Open Tray, unperforated | 11.4335 | 36.4335 | 0.2 | 30 | 30.986
3 | Cat5e/s (AWG24) | 1 | 5 | 9.5 | 25 | 24 | 50 | 4.5199 | 0.68541 | B: Closed Trunking/Conduit | 8.906 | 33.906 | 0.2 | 20 | 20.5562
PC2 | Patch Cord at TO side | 0.66667 | 6 | 13 | 25 | 1 | 0 | 0 | 1 | E/F: Ventilated | 1.3563 | 26.3563 | 0.2 | 5 | 7.5953
[11 empty] | Planned PL length (m) |  |  |  | 90
| Yellow fields can be modified | [9 empty] | Planned Channel length (m) |  |  |  | 100
[11 empty] | Electrical Channel length @ 20°C (m): |  |  |  | 108.6916
[11 empty] | Electrical Channel length reserve (m): |  |  |  | 0.30844
Note: | Specific values are based on R&Mfreenet cable assortment and formulas have been verified with it. No guarantee can be made for other manufacturer's products. | [9 empty] | Tglobal (°C) |  |  |  | 37.7081
[11 empty] | Allowed Channel length @ T global (m) |  |  |  | 100.3167
Recommended connectivity:
[8 empty] | R&Mfreenet RJ45 Module: |  |  |  | Cat.5e or Cat.6
[8 empty] | R&Mfreenet RJ45 Patchcord with IDC: |  |  |  | Cat.5e
Project / System - Identification: | [7 empty] | Planned by:
Note on F3: Gerber Matthias: Average current in a bundle generated by different levels of PoE applications.
Note on F5: Gerber Matthias: Definition whether cabling is: - shielded: /s - unshielded: /u
Note on C7: Gerber Matthias: AWG24: 1.2 AWG26: 1.5 AWG28/30: 2.0
Note on C8: Gerber Matthias: Max. cable temperature range according to data sheet (typically 60°C)
Note on F8: Gerber Matthias: The standards assume that all cabling types behave the same. The better cooling properties of shielded cables in a bundle are not considered. With STP Prio: "Yes" the real temperature in a bundle are used for calculation With STP Prio: "No" the temperature increase according the standard is used.
Note on H10: Gerber Matthias: Number of cables in the conduit or bundle
Note on I10: Tray size in mm, if present. Width of cable bundle in rectangular arangement. For circular bundels or tube conduit: 0 mm
Note on J10: Gerber Matthias: The standard calculates round bundles only. With rectangular cable arrangement the temperature increase will be reduced based on width to height ratio
Note on K10: Gerber Matthias: This is the reduction factor for temperature increase based on width to height ratio
Note on L10: Installation Condition: E/F: Ventilated C: Open Unperforated Tray B: Trunking / Conduit A: Insulation

## Printout
Permanent Link length calculator according to ISO/IEC 14763-2 and EN 50174-2:
PoE-Application: |  | RP3 |  |  |  |  | Power: | 90 | W
Class: |  | D
Connectors in Channel |  | 2 |  | Shielding: | /s |  | Note: | No restrictions on the use of 4PPoE. Temperature increase expected.
Total patchcord length: |  | 10 | m
Patchcord coefficient: |  | 1.5
Max. cable temprature: |  | 60 | °C | STP Prio: | No
Link segment no. | Cable type |  | Ambient temperature (°C) | Number of cables | Conduit width (mm) | Installation condition | Bundle reduction factor | Temp. increase bundle (°C) | Total temp. (ambient + increase) (°C) | Planned segment length (m) | Normalized electrical length at 20 °C (m)
PC1 | Patch Cord at Patch Panel side |  | 35 | 24 | 0 | E/F | 1 | 8.6312 | 43.6312 | 5 | 7.8545
1 | Cat5e/s (AWG24) |  | 25 | 200 | 200 | E/F | 0.52858 | 16.2437 | 41.2437 | 40 | 41.6995
2 | Cat5e/s (AWG24) |  | 25 | 75 | 100 | C | 0.62129 | 11.4335 | 36.4335 | 30 | 30.986
3 | Cat5e/s (AWG24) |  | 25 | 24 | 50 | B | 0.68541 | 8.906 | 33.906 | 20 | 20.5562
PC2 | Patch Cord at TO side |  | 25 | 1 | 0 | E/F | 1 | 1.3563 | 26.3563 | 5 | 7.5953
[7 empty] | Planned PL length (m) |  |  |  | 90
[7 empty] | Planned Channel length (m) |  |  |  | 100
[7 empty] | Electrical Channel length reserve (m): |  |  |  | 0.30844
[7 empty] | Tglobal (°C) |  |  |  | 37.7081
Project / System - Identification: | [5 empty] | Planned by:

## Presets (hidden)
Installation condition | Cable coefficient | Attenuation coefficient | Electrical length | Cable multiplicator | Application | Class | EMC Protection | Connectors | Patchcord | STP prio: | Cable /u | Cable /s
E/F: Ventilated | 5 | 0.4 | 109 | 1 | RP1 | D | /s | 2 | 1.2 | Yes | Cat5e/u (AWG24) | Cat5e/s (AWG24)
C: Open Tray, unperforated | 3 | 0.2 | 104 | 1.05 | RP2 | E | /u | 3 | 1.5 | No | Cat6/u (AWG24) | Cat6/s (AWG23)
B: Closed Trunking/Conduit | 2.5 |  |  | 1.1 | RP3 | EA |  | 4 | 2 |  | Cat6/u (AWG23) | Cat6A/s (AWG23) |  | 0.75 | 1 | 0.92689
A: Insulation |  |  |  | 1.15 |  | F |  |  |  |  | Cat6A/u (AWG23) | Cat7/s (AWG23) |  | 1 | 0.89 | 0.9078
[6 empty] | FA |  |  |  |  | Cat6A/u (AWG23) WARP | Cat7/s (AWG22) |  | 2 | 0.84 | 0.8358
[11 empty] | Cat6A/u (AWG22) WARP | Cat7A/s (AWG22) |  | 3 | 0.77 | 0.7708
[11 empty] | NA | NA |  | 4 | 0.71 | 0.7128
| Power | Text | [8 empty] | Class D /u (AWG26) | Class EA /s (AWG26, 60m) |  | 5 | 0.66 | 0.6618
RP1 | < 30 | Number of PoE devices allowed is restricted based on device PoE type. No Temperature increase expected. |  |  |  | 0 |  |  |  |  | Class E /u (AWG26) | Class EA /s (AWG22, 105m) |  | 6 | 0.62 | 0.6178
RP2 | 30-80 | Number of PoE devices allowed is restricted based on device PoE type. Limited Temperature increase expected. | I average: | 0.5 | A | [5 empty] | Class EA /u (AWG26) | Class EA Bundle (AWG26) |  | 7 | 0.59 | 0.5808
RP3 | 90 | No restrictions on the use of 4PPoE. Temperature increase expected. |  |  |  | 0.5 |  |  |  |  | Cat6A/u Bundle (AWG23) WARP | Cat6A/s Bundle (AWG23) |  | 8 | 0.56 | 0.5508
[14 empty] | 9 | 0.53 | 0.5278
[14 empty] | 13 |  | 0.4638
E/F: Ventilated | 0.2312 |  |  |  |  | /s | 0.2 | [6 empty] | 14 |  | 0.4478
C: Open Tray, unperforated | 0.3088 |  |  |  |  | /u | 0.4 | [6 empty] | 15 |  | 0.4318
B: Closed Trunking/Conduit | 0.48 | [12 empty] | 16 |  | 0.4158
A: Insulation | 1.08
[14 empty] | 17 |  | 0.3998
1.2 | 5.5 | 9.5 | [11 empty] | 18 |  | 0.3838
1.5 | 6 | 13 | [11 empty] | 19 |  | 0.3678
2 | 4.5 | 17.8 | [11 empty] | 20 |  | 0.3518
[11 empty] | Bundle to Ambient Factor | Formula factor 29125 | J26
| Diameter | Resistance | D | E | EA | F | FA | Attenuation | Shielded correction coefficient | Picture ref. | Cu (F/UTP) = 5 | 3.174 | 0
Cat5e/u (AWG24) | 5 | 9.5 | 1 | NA | NA | NA | NA | 0.4 | 0 | 6 | Cu (F/UTP) = 3 | 1.9 | 1.274
Cat5e/u (AWG22) | 0.01 | 0 | NA | NA | NA | NA | NA | 0.4 | 0 | 6 | Cu (S/FTP) = 2.75 | 1.75 | 1.424
Cat6/u (AWG24) | 5.7 | 8.5 | 1 | 1 | NA | NA | NA | 0.4 | 0 | 6
Cat6/u (AWG23) | 6 | 7.5 | 1.05 | 1 | NA | NA | NA | 0.4 | 0 | 6
Cat6A/u (AWG23) | 9 | 9.5 | 1.1 | 1.05 | 1 | NA | NA | 0.4 | 0 | 6
Cat6A/u (AWG23) WARP | 7.2 | 9.5 | 1.1 | 1.05 | 1 | NA | NA | 0.4 | 1.274 | 6
Cat6A/u (AWG22) WARP | 7.6 | 6.5 | 1.15 | 1.1 | 1.05 | NA | NA | 0.4 | 1.274 | 6
NA | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class D /u (AWG26) | 5.5 | 13 | 0.666 | NA | NA | NA | NA | 0.4 | 0 | 6
Class E /u (AWG26) | 5.5 | 13 | 0.666 | 0.666 | 0.666 | 0.666 | 0.666 | 0.4 | 0 | 6
Class EA /u (AWG26) | 5.5 | 13 | 0.666 | 0.666 | 0.666 | 0.666 | 0.666 | 0.4 | 0 | 6
Cat6A/u Bundle (AWG23) WARP | 7.2 | 10.5 | 1 | 0.95 | 0.9 | NA | NA | 0.4 | 0 | 6
Cat5e/s (AWG24) | 5 | 9.5 | 1 | NA | NA | NA | NA | 0.2 | 1.274 | 5
Cat6/s (AWG23) | 7.5 | 7.5 | 1.05 | 1 | NA | NA | NA | 0.2 | 1.274 | 5
Cat6A/s (AWG23) | 7.5 | 7.5 | 1.1 | 1.05 | 1 | 1 | NA | 0.2 | 1.424 | 5
Cat7/s (AWG23) | 7.5 | 7.5 | 1.1 | 1.05 | 1 | 1 | NA | 0.2 | 1.424 | 5
Cat7/s (AWG22) | 8.5 | 6 | 1.15 | 1.1 | 1.05 | 1 | 1 | 0.2 | 1.424 | 5
Cat7A/s (AWG22) | 8.5 | 6 | 1.15 | 1.1 | 1.05 | 1 | 1 | 0.2 | 1.424 | 5
NA | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Class EA /s (AWG26, 60m) | 6 | 13 | 0.666 | 0.666 | 0.666 | 0.666 | 0.666 | 0.2 | 1.424 | 5
Class EA /s (AWG22, 105m) | 8.5 | 5.5 | 1.2 | 1.2 | 1.18 | 1.1 | 1.05 | 0.2 | 1.424 | 5
Class EA Bundle (AWG26) | 6 | 13.8 | 0.666 | 0.64 | 0.61 | 0.61 | NA | 0.2 | 1.424 | 5
Cat6A/s Bundle (AWG23) | 7.5 | 8 | 1 | 0.95 | 0.9 | 0.9 | NA | 0.2 | 1.424 | 5
D | 109 | 107 | 105 | 4 |  | Cat.5e or Cat.6
E | 104 | 103 | 102 | 5 |  | Cat.6 or Cat.6A EL
EA | 104 | 103 | 102 | 6 |  | Cat.6A EL or Cat.6A
F | 105 | 103 | 102 | 7 |  | NA
FA | 105 | 103 | 102 | 8 |  | NA
|  | /s | /u | /s | /u | /s | /u | /s | /u
D | Cat.5e or Cat.6 |  |  | Presets!c61 | Presets!d61 | Presets!i61 | Presets!j61 |  |  | Cat.5e
E | Cat.6 or Cat.6A EL |  |  | Presets!c62 | Presets!d62 | Presets!i62 | Presets!j62 |  |  | Cat.6
EA | Cat.6A EL or Cat.6A |  |  | Presets!c63 | Presets!d63 | Presets!i63 | Presets!j63 |  |  | Cat.6A
F | NA |  |  | Presets!c64 | Presets!d64 | Presets!i64 | Presets!j64 |  |  | NA
FA | NA |  |  | Presets!c65 | Presets!d65 | Presets!i65 | Presets!j65 |  |  | NA
Presets!c61
Presets!i61
Note on N25: Gerber Matthias: Equals 3.2 in 14763-2 and 50174-2